Reg.No. ____________

UNIVERSITY

(Karunya Institute of Technology & Sciences)

(Declared as Deemed-to-be University under Sec.3 of the UGC Act, 1956)

End Semester Examination – Nov/Dec – 2016

|  |  | Semester : | 2016-17 ODD |
| --- | --- | --- | --- |
| Code : | 14EI2024 | Duration : | 3hrs |
| Sub. Name : | Power Plant Instrumentation | Max. marks : | 100 |

ANSWER ALL QUESTIONS (5 x 20 = 100 Marks)

| Q. No | Sub Div. | Questions | Course Outcome | Marks |
| --- | --- | --- | --- | --- |
| 1. | a. | Explain the block diagram of nuclear energy generation system. | CO1 | 15 |
|  | b. | List the parameters measured in wind energy system. | CO1 | 5 |
| (OR) |  |  |  |  |
| 2. | a. | Discuss in detail about the process involved in thermal power generation. | CO1 | 10 |
|  | b. | Mention the merits of solar power generating system based on cost, safety, and pollution. | CO2 | 4 |
|  | c. | Write short notes on the objectives of instrumentation in power plants. | CO1 | 6 |
| 3. | a. | With a neat sketch explain the hydro electric power generation system. | CO1 | 10 |
|  | b. | Design and explain in detail about the thermal and electrical control room present in a thermal power plant. | CO3 | 10 |
| (OR) |  |  |  |  |
| 4. | a. | Draw P&I diagram for flow transmitter orifice type and Final Control Element. | CO3 | 2 |
|  | b. | Identify the significance of condensation pot in flow measurement system with suitable diagram. | CO2 | 6 |
|  | c. | Design a V/I converter used in process industries. | CO3 | 12 |
| 5. | a. | Feed water flow to the boiler is measured with orifice plate sensor designed to give the maximum differential pressure of 10m for 120 T/hr water flow. The differential pressure transmitter is used for converting the differential pressure to a 4-20mA dc linear signal. A square root extractor circuit is introduced to convert the current signal to a voltage signal (1-5 V) linear to flow rate. Design measurement system for the above problem and give the calibration chart for calibrating the transmitter along with square root extractor. | CO3 | 14 |
|  | b. | Explain the working of potential transformer. | CO1 | 6 |
| (OR) |  |  |  |  |
| 6. | a. | Suggest and explain a suitable instrument for conductivity measurement of feed water. | CO2 | 6 |
|  | b. | Explain the pollution gas monitoring system using Infrared Flue Gas Analyzer. | CO1 | 10 |
|  | c. | A Coal conveyor system moves at a speed of 450 m/min. Weighing platform is 15m in length and a particular weighing shows a reading of 200Kg. Find the coal delivery in T/hr. | CO3 | 4 |
| 7. | a. | Explain the oxygen measurement in flue gas using paramagnetic oxygen analyzer. | CO2 | 10 |
|  | b. | Elaborate the working principle of smoke detector and dust monitor. | CO1 | 10 |
| (OR) |  |  |  |  |
| 8. | a. | Explain the measurement system for CO and CO2 in flue gas. | CO1 | 10 |
|  | b. | Write the principle of coal quantity measurement. | CO1 | 6 |
|  | c. | Calculate the feed flow rate in conveyor if the load is 200 Kg/m and belt speed is 20m/min. | CO3 | 2 |
|  | d. | Differentiate forced draft and induced draft system. | CO2 | 2 |
|  |  | Compulsory: |  |  |
| 9. | a. | Explain the schemes of steam temperature control system. | CO1 | 8 |
|  | b. | Discuss about the hardware and software system of DCS for power plant automation with necessary diagram. | CO3 | 12 |