# Reg. No. ________

Karunya University

(Karunya Institute of Technology and Sciences)

(Declared as Deemed to be University under Sec.3 of the UGC Act, 1956)

End Semester Examination – April/May-2013

# Subject Title: WIND ENERGY		                      					 	 Time: 3 hours

# Subject Code: 12EE318				       	        				 	 Maximum Marks: 100

Answer ALL questions (5 x 20 = 100 Marks)

1.	a.	A 2.4 MW wind turbine has an installed cost of $2.4 x 106. Assume that the annual operating and 	maintenance costs are 2% of the initial installed cost. The wind regime at this site results in a 	capacity factor (CF) of 0.35. It is also assumed that the lifetime of this turbine is 25 years and 	that the electrical output can be sold for $0.05/ kWh. For a 5% discount rate, calculate the 	following economic parameters for this system:

i.	Simple payback period.													(2.5)

ii.	The net present value of the savings (NPVS).								(2.5)

iii.	The benefit-cost ratio (B/C).												(2.5)

iv.	The levelized cost of energy (COEL).										(2.5)

b.	A proposed wind farm installation is based on the use of thirty 2 MW wind turbines. The installed capital cost is estimated at $1000/kW and the annual operation and maintenance costs are estimated to be 3% of the original capital cost. Financing for the project is to come from two sources: 	i.	 A 20 year loan at 7% (75%), and 		ii.	an equity investment that has a return of 15% (25%). The average capacity factor of the wind farm is estimated to be 0.35. Determine the estimated cost of energy ($/kWh) from this proposed wind farm.						(10)

(OR)

2.	Elaborate on the following topics pertaining to wind energy:

a.	National Renewable Energy Policies.												(5)

b.	Carbon tax and green credits.														(5)

c.	Energy trading.																(5)

d.	Funding for wind energy projects.													(5)

3.	Compulsory:

- A wind turbine with a rotor diameter of 55 m is rated at 1 MW at a hub height wind speed of 14 m/s. It has a cut-in speed of 4 m/s and a cut-out speed of 25 m/s. Assume that this machine is located at a site where the mean wind speed is 10 m/s and that a Rayleigh wind speed distribution can be used. Calculate the number of hours per year that the wind is below the cut-in speed and the number of hours per year that the machine will be shut down due to wind speeds above the cut-out velocity.																(5)

b.	Two wind turbines emitting 105 dB (A) at the source are located 200 m and 240 m away from a location of interest. Calculate the sound pressure level (in dB (A)) at the point of interest from the combined acoustic effect of the two turbines. Assume a sound absorption coefficient of 0.005 dB (A)/m.																	(5)

c.	Discuss in detail about wind measurement and instrumentation.				    	      		(10)

4.	a.	Find θ, θP, and c for one blade section from r/R = 0.45 to r/R = 0.55 (centered on r/R = 0.50) for 	an ideal blade (assume Cd = 0, a′ = 0). Assume λ =7, B=3, R=5 m, and Cl =1.0 and the minimum 	Cd / Cl occurs at α = 7.  Find Urel when a=1/3.										(5)

b.	A wind turbine rotor turning at 60 rpm is brought to a stop by a mechanical brake. The rotor 	inertia is 13,558 kg m2.															(5)

i.	What is the kinetic energy in the rotor before it is stopped? How much energy does the 			brake absorb during the stop?

ii.	Suppose that all the energy is absorbed in a steel brake disc with a mass of 27 kg. Ignoring 		losses, how much does the temperature of the steel brake disc rise during the stop? Assume 		a specific heat for steel of 0.46 kJ/kg C.

c.	Discuss the various wind turbine topologies.									 	(10)

(OR)

[P.T.O]

5.	a.	Write a brief note on the loads on wind turbines.										(5)

b.	Write down the procedure for generalized rotor design of a wind turbine with appropriate 			expressions.																 	(15)

6.	a.	A resistive load of 500 kW at 480 V is supplied by an eight-pole synchronous generator, 			connected to a diesel engine, and a wind turbine with an induction generator. The synchronous 		machine is rated to produce 1000 kVA. Its synchronous reactance is 0.4 Ohms. A voltage 			regulator maintains a constant voltage of 480 V across the load and a governor on the diesel 			engine maintains a fixed speed. The speed is such that the grid frequency is 60 Hz. The power 		system is three-phase, and the electrical machines are both Y-connected. The power from the 		wind is such that the induction generator is operating at a slip of -0.01. At this slip, the power is 		153.5 kW and the power factor is 0.888. Find the synchronous generator’s speed, power factor 		and power angle.				     												(10)

b.	Describe in brief the different power converters used in wind turbines with neat diagrams.       																					(10)

(OR)

7.	Discuss in detail the electrical aspects of variable speed wind turbines.

8.	a.	Consider a wind turbine generator connected to a grid system as shown in figure with a line-	neutral system voltage, VS. The voltage at the wind turbine, VG, is not necessarily the same as VS. 	The distribution system resistance is R, and the distribution system reactance is X. The real 	generated power is P and the reactive power consumed by the wind turbine generator is Q. 	Suppose R = 8.8 Ω, X = 4.66 Ω, Vs = 11 kV, P = 313 kW, Q = 162 kVAr and the power factor at 	the generator is pf = 0.89. Determine the voltage difference between the grid and the generator, 	the voltage drop as a percent of the grid voltage, the fault level at the generator and the installed 	generator capacity as a percent of the fault level.										(10)

b.	Discuss in brief about the operational issues of wind turbines.					    		(10)

(OR)

9.	a.	A small community has 2000 residents and each of them consumes an average of 100 litres of 		water per day. They have access to an aquifer 100 m below ground level and are considering 		acquiring a wind electric water pump to bring the water to the surface. What would be the rated 		power of wind turbine (kW) that would pump, on the average, an amount of water equal to what 		the community uses? Assume that the capacity factor of the wind turbine is 0.25 and that the 			efficiency of the water pump is 80%.												 (6)

- “The design of hybrid power systems depends on the specifics of the existing power system and on the match of the load and the available renewable resource.” Discuss in detail the hybrid system design issues and the hybrid system components.		      						(14)