# Reg. No. ________

Karunya University

(Karunya Institute of Technology and Sciences)

(Declared as Deemed to be University under Sec.3 of the UGC Act, 1956)

End Semester Examination – April/May-2013

# Subject Title: DESIGN OF THERMAL POWER EQUIPMENTS			 Time: 3 hours

# Subject Code: 12ME303				         		        	         	  Maximum Marks: 100

Answer ALL questions (5 x 20 = 100 Marks)

1.	Compulsory

a.	Enumerate the various causes for heat losses in the steam generators. 			(10)

b.	The following data refer to a boiler plant consisting of an economizer, a boiler and a 	superheater:

Mass of water evaporated per hour = 5940 kg, mass of coal burnt per hour = 675 kg, L.C.V. of coal = 31600 kJ	/ kg, pressure of steam at boiler stop valve = 14 bar, temperature of feed water entering the economizer = 32˚C, temperature of feed water leaving the economizer = 115˚C, dryness fraction of steam leaving the boiler and entering the superheater is 0.96, temperature of steam leaving the superheater = 260˚C, specific heat of superheater steam = 2.3 kJ / kg.K. Determine:

i.	 Percentage of heat in coal utilized in economizer, boiler and superheater.

ii.	 Overall efficiency of boiler plant.										(10)

2.	a.	List the principal objectives to be considered in the design of power plant boilers.(6)

b.	Mention the important factors required to be considered in the design of a furnace of 			boiler power plants.														(5)

c.	Explain the various classifications of furnace walls.							(9)

(OR)

3.	a.	Describe the construction and operation of the following:

i. 	Travelling grate stoker.

ii. 	Underfeed stoker (retort type).											(10)

b.	With a neat sketch explain the salient features of a wet bottom furnace. 			(10)

4.	a.	Differentiate between natural and forced circulation employed in power plant boilers.

(4)

b.	Define ‘circulation ratio’ in the case of forced circulation.						(2)

c.	A furnace wall riser, 18 m long, 76.2 mm OD and 6.1 mm thick receives saturated water 	at 80 bar and 1.5 m/s velocity. Assuming a circulation ratio of 12.5 and a slip ratio of 1.2, 	determine 	i.	the pressure head developed	ii.	the void fraction at riser exit

iii.	 the 	heat transfer rate per unit projected area of the riser tube.				(14)

(OR)

5.	a.	Define with respect to a cooling tower:

i.	 Approach 	ii.	Range 	iii.	Cooling 	efficiency.						(6)

b.	During a trial on a steam condenser, the following observations were recorded:

Condenser vacuum = 680 mm of Hg, Barometer reading = 764 mm Hg, Mean condenser temperature = 36.2˚C, Hot well temperature = 30˚C, Condensate formed per hour = 1780 kg, Circulating cooling water inlet temperature = 20˚C, Circulating cooling water outlet temperature = 32˚C, Quantity of cooling water = 1250 kg/min. Determine the following:

i.	Vacuum efficiency.

ii.	Condenser efficiency.

iii.	Condition of steam entering the condenser.

iv.	Mass of air present.													(14)

[P.T.O]

6.	a. 	Write brief notes on the following troubles caused by the impurities in water. Scale 	formation, Corrosion, Carry over, and Embrittlement.							(12)

b.	What are the various methods of feed water treatment? Explain how ‘thermal treatment’ 		is done with the help of a neat sketch of ‘deaerating heater’.					(8)

(OR)

7.	a.	Describe with neat sketches the following mechanical separators used in power plant      	boilers: Baffles/ Screens and Cyclones.										(6)

b.	How is % Boiler blowdown expressed?										(2)

c.	Steam leaves the drum of a boiler at the rate of 64 kg/s at 60 bar, with 2% moisture. The feedwater from the economizer enters the drum at the rate of 62 kg/s and has 3 ppm. The makeup water at the rate of 2 kg/s is fed into the drum and it has 50 ppm. Effective steam washing reduces the solids in the moisture, leaving the drum with the steam, to 5 ppm. If the solid concentration in the drum water is to be maintained at 1000 ppm, find,

i.	the blowdown required in kg/s		ii. 	heat loss in blowdown as a percentage of total heat released in the furnace , if blowdown heat recovery is not used, when the fuel burning rate is 7 kg/s and its heating value 23 MJ/kg 		iii.	the deposition of scale in superheater tube in kg/day. Take the ambient temperature as 30˚C.				(12)

8.	a.	State the relationship for rate of heat transfer from gas to air in an air pre-heater. 	(2)

b.	How does a ‘regenerative type’ air pre-heater differ from a ‘recuperative type’ air pre-	heater? Explain any one type with a neat sketch.								(6)

c.	In a steam generator, tubular type air pre-heater is used. The hot flue gases at a temperature of 450˚C flow over the air pre-heater coils at the rate of 1250 kg/s and are cooled to 160˚C. Air entering at 35˚C flows outside the tubes at the rate of 1167 kg/s. The inlet velocity of flue gases is 13 m/s and the tubes are of 60 mm inner dia and 65 mm OD. If the overall heat transfer coefficient is 30 W/m2K, find the length and the number of tubes. Assume that the flue gases behave as an ideal gas having cp = 1.10 and R = 0.287 kJ/ kg.K.														(12)

(OR)

9.	a.	Explain the construction and operation of an electrostatic precipitator with a neat sketch.																				(10)

b.	Determine the height and diameter of chimney used to produce a draught for a boiler which has an average coal consumption of 1800 kg/h. and flue gases formed per kg of coal fired are 14 kg. The pressure losses through the system are given below:

Pressure loss in the fuel bed = 7 mm of water, pressure loss in boiler flue = 7 mm of water, pressure loss in bends = 3 mm of water, pressure loss in chimney = 3 mm of water, pressure head equivalent to velocity of flue gases passing through the chimney = 1.3 mm of water. The temperature of ambient air and flue gases are 35˚C and 310˚C respectively. Assume actual draught is 80 % of theoretical.					(10)