Reg.No. ____________

End Semester Examination – Apr/May – 2018

| # Code : 14EE2016 |  |  | # Duration : | # 3hrs |
| --- | --- | --- | --- | --- |
| # Sub. Name : POWER SYSTEM PROTECTION AND SWITCHGEAR |  |  | # Max. marks : | # 100 |

ANSWER ALL QUESTIONS (5 x 20 = 100 Marks)

| Q. No. | Sub Div. | Questions | Course Outcome | Marks |
| --- | --- | --- | --- | --- |
| 1. |  | Interpret the construction and working principle of induction type non-directional overcurrent relay. | CO1 | 20 |
| (OR) |  |  |  |  |
| 2. | a. | Determine the actual time of operation of a 5ampere, 3 second over current relay having a current setting of 125% and a time setting multiplier of 0.6 connected to supply circuit through a 400/5 current transformer when the circuit carries a fault current of 4000A.Time of operation is 3.5 seconds for the estimated value of P.S.M. | CO1 | 5 |
|  | b. | Narrate the construction, working principle and characteristics of reactance relay type distance relay. | CO1 | 15 |
| 3. | a. | Quote the basic elements of static relay. | CO1 | 5 |
|  | b. | Draw and explain the construction and working of Buchholz relay. Against which faults Buchholz relay gives protection. | CO1 | 15 |
| (OR) |  |  |  |  |
| 4. | a. | Select a suitable relay to protect the three phase Induction motor during overload condition and explain with neat diagram. | CO2 | 14 |
|  | b. | List the abnormal conditions and faults that occur in generator. | CO2 | 6 |
| 5 | a. | A 3-phase 500kVA, 440V/11kV transformer is connected in star/ delta. The protection transformer on the LV side have turns ratio of 500/5. What will be the C.T. ratio on the HV side of the transformer? | CO2 | 8 |
|  | b. | Illustrate restricted earth-fault protection for generators. | CO2 | 12 |
| (OR) |  |  |  |  |
| 6. | a. | In a system of 132kV the circuit phase to ground capacitance is 0.01mf, the series inductance is 6H. Calculate voltage appearing across the contact of circuit breaker and the value of the resistance to be used across contact space to eliminate the restriking voltage. | CO2 | 6 |
|  | b. | Outline short notes on the followings: (i) Current chopping phenomenon. (ii) Resistance switching | CO3 | 14 |
| 7. | a. | Sketch and formulate the constructional details, working principle of minimum oil circuit breaker. | CO3 | 12 |
|  | b. | Illustrate the merits and demerits of SF6 circuit breaker. | CO3 | 8 |
| (OR) |  |  |  |  |
| 8. |  | Demonstrate the following types of arrestres: (a) Horn gap arresters (b) Rod gap arresters (c) Expulsion type arresters (d) Valve type arresters | CO2 | 20 |
|  |  | Compulsory: |  |  |
| 9. | a. | Write short notes on protection against over voltages due to travelling waves. | CO2 | 10 |
|  | b. | Categorize the operation of various types of surge obserbers. | CO2 | 10 |