Reg.No. _____________

End Semester Examination – Apr/May – 2018

| # Code : | # 17ME3028 | # Duration : | # 3hrs |
| --- | --- | --- | --- |
| # Sub. Name : | # DESIGN OF THERMAL POWER EQUIPMENT | # Max. marks : | # 100 |

ANSWER ALL QUESTIONS (5 x 20 = 100 Marks)

| Q. No. | Sub Div. | Questions | Course Outcome | Marks |
| --- | --- | --- | --- | --- |
| 1. | a. | Enumerate the principal objectives for the design of modern power station boilers. | CO1 | 8 |
|  | b. | Describe the primary classifications of furnace walls in use. | CO1 | 12 |
| (OR) |  |  |  |  |
| 2. | a. | How is a steam boiler defined under Indian Boiler Regulations Act? Mention the different stages that are covered by a typical IBR inspection. | CO1 | 10 |
|  | b. | How is the heat release rate per unit wall area of the burner region estimated? With neat sketches explain the various furnace bottoms. | CO1 | 10 |
| 3. | a. | A furnace wall riser 18 m long 76.2 mm outer dia and 6.1 mm thick receives saturated water at 80 bar and 1.5 m/s velocity. Assuming a circulation ratio of 12.5 and a slip ratio of 1.2, determine i) the pressure head developed, ii) the void fraction at riser exit and iii) the heat transfer rate per unit projected area of the riser tube. | CO2 | 12 |
|  | b. | A surface condenser receives 250 t/h of steam at 40C with 12 % moisture. The cooling water enters at 32C and leaves at 38C. The pressure inside the condenser is found to be 0.078 bar. The velocity of circulating water is 1.8 m/s. The condenser tubes are of 25.4 mm outer dia and 1.25 mm thickness. Taking the overall heat transfer coefficient as 2600 W/m2K, determine i) the rate of cooling flow of water ii) the length of tubes iii) the number of tubes. | CO5 | 8 |
| (OR) |  |  |  |  |
| 4. | a. | How will you define void fraction? Express void fraction in terms of specific volume (vg, vf), dryness fraction (x) and slip ratio (S) in the case of two-phase flow in a riser. | CO2 | 10 |
|  | b. | How are cooling towers employed in thermal power plants classified? Explain any two with neat sketches. | CO5 | 10 |
| 5. | a. | A boiler produces 200 kg of dry and saturated steam per hour at 10 bar and feed water is heated by an economizer to a temperature of 110C. 225 kg of coal of a calorific value of 30100 kJ/kg are fired per hour. If 10 % of coal remains unburnt, find the thermal efficiency of the boiler and boiler and grate combined. | CO2 | 10 |
|  | b. | A steam generator evaporates 18000 kg/h of steam at 12.5 bar and a quality of 0.97 from feed water at 105C, when coal is fired at the rate of 2040 kg/h. If the higher calorific value of the coal is 27400 kJ/kg, find i) the heat rate of boiler in kJ/h, ii) the equivalent evaporation iii) the thermal efficiency. | CO2 | 10 |
| (OR) |  |  |  |  |
| 6. | a. | Is there a limit in superheating steam in a boiler? Justify your answer. Explain the different methods involved in desuperheating and attemperation. | CO3 | 10 |
|  | b. | Elaborate the design considerations of reheaters in a thermal power plant. | CO3 | 10 |
| 7. | a. | Bring out the necessity of steam washing? How is steam washing carried out in modern power plant boilers? | CO6 | 10 |
|  | b. | Write briefly on i) Chemical treatment and ii) Mechanical carry over. | CO6 | 10 |
| (OR) |  |  |  |  |
| 8. | a. | Describe briefly various methods of steam purification. | CO6 | 10 |
|  | b. | Describe the causes and effects of silica carry over in boilers. How is the issue tackled? | CO6 | 10 |
|  |  | Compulsory: |  |  |
| 9. | a. | Compute the motor capacity required for the forced draught fan under conditions stated below: Coal rate:10 tonnes/h Coal analysis: Carbon 78.0, Hydrogen 3.0, Oxygen 3.0, Sulphur 1.0, Moisture 7.0, Ash 8.0 Excess air : 30% Plenum chamber pressure : 180 mm water gauge Mechanical Efficiency of fan : 60% Ambient temperature : 30C | CO4 | 7 |
|  | b. | A 200 m high 4 m dia chimney emits 1000 kg/s of 100C gases into 5C air. The prevailing wind velocity is 50 km/h. The atmosphere is in a condition of neutral stability. Calculate the height of gas plume. | CO4 | 6 |
|  | c | Explain ash separation by electrostatic precipitation. Illustrate your answer with a neat sketch. | CO4 | 7 |