Reg.No. ____________

End Semester Examination – Nov/Dec - 2017

| Code : | 14EE2013 | Duration : | 3hrs |
| --- | --- | --- | --- |
| Sub. Name : | TRANSMISSION AND DISTRIBUTION | Max. marks : | 100 |

ANSWER ALL QUESTIONS (5 x 20 = 100 Marks)

| Q. No. | Sub Div. | Questions | Course Outcome | Marks |
| --- | --- | --- | --- | --- |
| 1. | a. | Sketch a typical Alternating Power Supply System and mark the voltage levels from generation, through transmission up to distribution systems. | CO1 | 10 |
|  | b. | A generating station has the following daily load cycle. Draw the following i. Load curve ii. Load Duration Curve iii. Maximum Demand iv. Units Generated/Day v. Average Load vi. Load Factor. Time (Hrs); 0-6; 6-10; 10-12; 12-16; 16-20; 20-24. Load (MW); 40; 50; 60; 50; 70; 40. | CO1 | 10 |
| (OR) |  |  |  |  |
| 2. | a. | A generating station has a maximum demand of 25MW, a load factor of 60%, a plant capacity factor of 50% and a plant use factor of 72%. Find i. the reserve capacity of the plant ii. the daily energy produced iii. maximum energy that could be produced daily if the plant while running as per schedule, were fully loaded. | CO1 | 8 |
|  | b. | Derive an expression for two phase four wire system. | CO1 | 12 |
| 3. |  | Deduce an expression for line to neutral capacitance for a 3-phase overhead transmission line when the conductors are i. symmetrically placed. ii. unsymmetrically placed but are completely transposed. | CO1 | 20 |
| (OR) |  |  |  |  |
| 4. | a. | A 3-phase, 50Hz transmission line 100 km long delivers 20 MW at 0.9 pf lagging and at 110 kV. The resistance and reactance of the line per phase per km are 0.2 ohm and 0.4 ohm respectively, while capacitance admittance is 2.5 x 10-6 siemen / km/ phase. i. Calculate the current and voltage at the sending end. ii. Efficiency of transmission. Use Nominal T method. | CO2 | 15 |
|  | b. | Define ABCD constants as applied to the performance of medium transmission lines by Nominal  method and explain. | CO2 | 5 |
| 5. | a. | Discuss the advantages and disadvantages of i. Pin type Insulators ii. Suspension type Insulators iii. Shackle type Insulator. | CO2 | 10 |
|  | b. | A 3-phase transmission line is being supported by three disc insulators. The potential across the top unit (i.e. nearer to tower) and middle unit are 8 kV and 11 kV respectively. Calculate the line voltage and string efficiency of the line. | CO2 | 10 |
| (OR) |  |  |  |  |
| 6. | a. | Deduce an expression for sag in overhead lines when i. Supports are at equal levels. ii. Supports are at unequal levels. | CO2 | 10 |
|  | b. | The towers of height 30 m and 90 m respectively support a transmission line conductor at water crossing. The horizontal distance between the towers is 500 m. If the tension in the conductor is 1600 kg, find the minimum clearance of the conductor and water and clearance mid-way between the supports. Weight of conductor is 1.5 kg/m. Bases of the towers can be considered to be at water level. | CO2 | 10 |
| 7. | a. | Draw a cross sectional view, showing the constructional details of a single core low tension cable and explain the purpose of each material used. | CO2 | 10 |
|  | b. | Calculate the capacitance and charging current of a single core cable used in a 3 phase 66 kV system. The cable is one kilometer long having a core diameter of 10 cm and an impregnated paper insulation of thickness 7 cm. The relative permittivity of the insulation may be taken as 4 and the supply at 50 Hz. | CO2 | 10 |
| (OR) |  |  |  |  |
| 8. | a. | Compare the merits and demerits of underground system versus overhead system. | CO2 | 10 |
|  | b. | A single-core 66 kV cable working on 3-phase system has a conductor diameter of 2 cm and a sheath of inside diameter 5.3 cm. If two inter sheaths are introduced in such a way that the stress varies between the same maximum and minimum in the three layers, find i. positions of inter sheaths ii. voltage on the inter sheaths iii. maximum and minimum stress. | CO2 | 10 |
|  |  | Compulsory: |  |  |
| 9. | a. | Explain the following systems of distribution i. Radial system ii. Ring main system iii. Interconnected system. | CO3 | 8 |
|  | b. | Describe any three types of dc distributors and derive the expression for the same. | CO3 | 12 |

ALL THE BEST